## Analysis Results
OCTAGONAL SPREAD FOOTING ANALYSIS
Job Information
Job Name | Turbine Hall Building
Job Number | Talin Power Plan
Subject | Vessel Tank
Originator | Roberto
Checker | Roberto
Input Data - Footing
Ftg. Base Length, Df | 8.6 | m
Ftg. Base Thickness, Tf | 0.7 | m
Oct. Pier Length, Dp | 8.6 | m
Oct. Pier Height, hp | 0.5 | m
Concrete Unit Wt., γc | 24 | kN/m³
Soil Depth, Ds | 1 | m
Soil Unit Wt., γs | 18 | kN/m³
Pass. Press. Coef., Kp | 0
Coef. of Base Friction, μ | 0.4
Uniform Surcharge, Q | 10 | kN/m²
SB Capacity, q_allow | 150 | kN/m²
Controlling Loading Data (LC: 110 LC110)
Applied Vert. Load, P | 3164.75 | kN
Applied Horiz. Load, H | 436.1 | kN
Applied Moment, M | 1618.4 | kN-m
Load Case | 110 LC110
Footing Base Properties
Dimension, Bf | 2.5189 | m
Footing Flat Side, Cf | 3.5622 | m
Footing Diagonal, Ef | 9.3086 | m
Footing Base Area, Af | 61.2705 | m²
Footing Volume, Vf | 42.8893 | m³
Footing Inertia, If | 299.4213 | m⁴
Pier Properties
Dimension, Bp | 2.5189 | m
Pier Flat Side, Cp | 3.5622 | m
Pier Diagonal, Ep | 9.3086 | m
Pier Area, Ap | 61.2705 | m²
Pier Volume, Vp | 30.6352 | m³
Pier, Surcharge, Soil, and Footing Base Weights
Pier Weight, Wp | 735.2456 | kN
Surcharge Load, Wq | 0 | kN
Soil Weight, Ws | 0 | kN
Ftg. Base Weight, Wf | 1029.3439 | kN
Total Resultant Load and Eccentricities
Total Vert. Load, ΣP | 4929.3395 | kN
Total Moment, ΣM | 2141.72 | kN-m
Eccentricity, e | 0.4345 | m
Eccentricity Ratio, e/Df | 0.0505
Overturning Check
Mr | 21196.16 | kN-m
Mo | 2141.72 | kN-m
FS(ot) | 9.8968
Sliding Check
Passive Resist., PR | 0 | kN
Frict. Resist., FR | 1971.7358 | kN
FS(slid) | 4.5213
Bearing Pressure (Axis through Corners)
Section Modulus, Sf | 64.3324 | m³
Brg. Distance Coef., K | 0
K*Df | 0 | m
%Brg. Area | 100 | %
Bearing Coef., L | N.A.
Gross Bearing, P(max) | 113.7436 | kN/m²
Gross Bearing, P(min) | 47.1606 | kN/m²
Net Press., Pmax(net) | 83.1436 | kN/m²
Bearing Pressure (Axis through Flat Sides)
Section Modulus, Sf | 69.6329 | m³
Brg. Distance Coef., K | 0
K*Df | 0 | m
%Brg. Area | 100 | %
Bearing Coef., L | N.A.
Gross Bearing, P(max) | 111.2094 | kN/m²
Gross Bearing, P(min) | 49.6948 | kN/m²
Net Press., Pmax(net) | 80.6094 | kN/m²
Summary of Results
FS(ot) | 9.897
FS(slid) | 4.521
%Brg. Area | 100 | %
Pmax(gross) | 113.744 | kN/m²
Pmax(net) | 83.144 | kN/m²
Design Check Ratios (Max across all Load Combinations)
Ratio Overturning | 0.101 | OK
Ratio Sliding | 0.2212 | OK
Ratio Soil BC | 0.0464 | OK
Ratio Max | 0.2212 | OK
Controlling Load Case | 110 LC110

## Load Combination Summary
LC | LC Name | P (kN) | H (kN) | M (kN-m) | Ds (m) | Ratio OT | Ratio SLD | Ratio SBC | Ratio Max
101 | 101 LC101 | 3164.75 | 0 | 0 | 1 | 0 | 0 | 0.0124 | 0.0124
102 | 102 LC102 | 3164.75 | 34.956 | 122.532 | 1 | 0.0078 | 0.0177 | 0.012 | 0.0177
103 | 103 LC103 | 3164.75 | 34.956 | 122.532 | 1 | 0.0078 | 0.0177 | 0.012 | 0.0177
104 | 104 LC104 | 3164.75 | 34.956 | 122.532 | 1 | 0.0078 | 0.0177 | 0.012 | 0.0177
105 | 105 LC105 | 3164.75 | 34.956 | 122.532 | 1 | 0.0078 | 0.0177 | 0.012 | 0.0177
106 | 106 LC106 | 3164.75 | 34.951 | 122.513 | 1 | 0.0078 | 0.0177 | 0.012 | 0.0177
107 | 107 LC107 | 3164.75 | 34.951 | 122.513 | 1 | 0.0078 | 0.0177 | 0.012 | 0.0177
108 | 108 LC108 | 3164.75 | 34.951 | 122.513 | 1 | 0.0078 | 0.0177 | 0.012 | 0.0177
109 | 109 LC109 | 3164.75 | 34.951 | 122.513 | 1 | 0.0078 | 0.0177 | 0.012 | 0.0177
110 | 110 LC110 | 3164.75 | 436.1 | 1618.4 | 1 | 0.101 | 0.2212 | 0.0088 | 0.2212
111 | 111 LC111 | 3164.75 | 436.1 | 1618.4 | 1 | 0.101 | 0.2212 | 0.0088 | 0.2212
112 | 112 LC112 | 3164.75 | 436.1 | 1618.4 | 1 | 0.101 | 0.2212 | 0.0088 | 0.2212
113 | 113 LC113 | 3164.75 | 436.1 | 1618.4 | 1 | 0.101 | 0.2212 | 0.0088 | 0.2212
114 | 114 LC114 | 3164.75 | 26.217 | 91.899 | 1 | 0.0058 | 0.0133 | 0.0121 | 0.0133
115 | 115 LC115 | 3164.75 | 26.217 | 91.899 | 1 | 0.0058 | 0.0133 | 0.0121 | 0.0133
116 | 116 LC116 | 3164.75 | 26.217 | 91.899 | 1 | 0.0058 | 0.0133 | 0.0121 | 0.0133
117 | 117 LC117 | 3164.75 | 26.217 | 91.899 | 1 | 0.0058 | 0.0133 | 0.0121 | 0.0133
118 | 118 LC118 | 3164.75 | 26.212 | 91.886 | 1 | 0.0058 | 0.0133 | 0.0121 | 0.0133
119 | 119 LC119 | 3164.75 | 26.212 | 91.886 | 1 | 0.0058 | 0.0133 | 0.0121 | 0.0133
120 | 120 LC120 | 3164.75 | 26.212 | 91.886 | 1 | 0.0058 | 0.0133 | 0.0121 | 0.0133
121 | 121 LC121 | 3164.75 | 26.212 | 91.886 | 1 | 0.0058 | 0.0133 | 0.0121 | 0.0133
122 | 122 LC122 | 3164.75 | 327.075 | 1213.8 | 1 | 0.0758 | 0.1659 | 0.0095 | 0.1659
123 | 123 LC123 | 3164.75 | 327.075 | 1213.8 | 1 | 0.0758 | 0.1659 | 0.0095 | 0.1659
124 | 124 LC124 | 3164.75 | 327.075 | 1213.8 | 1 | 0.0758 | 0.1659 | 0.0095 | 0.1659
125 | 125 LC125 | 3164.75 | 327.075 | 1213.8 | 1 | 0.0758 | 0.1659 | 0.0095 | 0.1659
126 | 126 LC126 | 3345.051 | 17.478 | 61.266 | 1 | 0.0037 | 0.0086 | 0.0118 | 0.0118
127 | 127 LC127 | 3345.051 | 17.478 | 61.266 | 1 | 0.0037 | 0.0086 | 0.0118 | 0.0118
128 | 128 LC128 | 3345.051 | 17.478 | 61.266 | 1 | 0.0037 | 0.0086 | 0.0118 | 0.0118
129 | 129 LC129 | 3345.051 | 17.478 | 61.266 | 1 | 0.0037 | 0.0086 | 0.0118 | 0.0118
130 | 130 LC130 | 3345.051 | 17.475 | 61.257 | 1 | 0.0037 | 0.0086 | 0.0118 | 0.0118
131 | 131 LC131 | 3345.051 | 17.475 | 61.257 | 1 | 0.0037 | 0.0086 | 0.0118 | 0.0118
132 | 132 LC132 | 3345.051 | 17.475 | 61.257 | 1 | 0.0037 | 0.0086 | 0.0118 | 0.0118
133 | 133 LC133 | 3345.051 | 17.475 | 61.257 | 1 | 0.0037 | 0.0086 | 0.0118 | 0.0118
134 | 134 LC134 | 160.866 | 34.956 | 122.532 | 0.6 | 0.0298 | 0.0681 | 0.0441 | 0.0681
135 | 135 LC135 | 160.866 | 34.956 | 122.532 | 0.6 | 0.0298 | 0.0681 | 0.0441 | 0.0681
136 | 136 LC136 | 160.866 | 34.956 | 122.532 | 0.6 | 0.0298 | 0.0681 | 0.0441 | 0.0681
137 | 137 LC137 | 160.866 | 34.956 | 122.532 | 0.6 | 0.0298 | 0.0681 | 0.0441 | 0.0681
138 | 138 LC138 | 160.866 | 34.951 | 122.513 | 0.6 | 0.0298 | 0.0681 | 0.0441 | 0.0681
139 | 139 LC139 | 160.866 | 34.951 | 122.513 | 0.6 | 0.0298 | 0.0681 | 0.0441 | 0.0681
140 | 140 LC140 | 160.866 | 34.951 | 122.513 | 0.6 | 0.0298 | 0.0681 | 0.0441 | 0.0681
141 | 141 LC141 | 160.866 | 34.951 | 122.513 | 0.6 | 0.0298 | 0.0681 | 0.0441 | 0.0681
142 | 142 LC142 | 160.866 | 12.04 | 44.674 | 0.6 | 0.0107 | 0.0234 | 0.0464 | 0.0464
143 | 143 LC143 | 160.866 | 12.04 | 44.674 | 0.6 | 0.0107 | 0.0234 | 0.0464 | 0.0464
144 | 144 LC144 | 160.866 | 12.04 | 44.674 | 0.6 | 0.0107 | 0.0234 | 0.0464 | 0.0464
145 | 145 LC145 | 160.866 | 12.04 | 44.674 | 0.6 | 0.0107 | 0.0234 | 0.0464 | 0.0464